

**SECTION XXXXXX**

**HEAT TRACING FOR GREASE WASTE PIPE**

1. GENERAL
   1. SECTION INCLUDES
      1. Factory fabricated and terminated Mineral Insulated (MI) heating cable assembly.
      2. Field terminated Constant Wattage (CW) heating cable.
      3. Thermostats
      4. Monitor/Control panels
      5. Pipe heat tracing accessories and installation material for a complete operating system.
   2. REFERENCES
      1. Canadian Standards Association (CSA).
      2. Factory Mutual (FM).
      3. National Electric Code (NEC).
      4. Underwriters Laboratories (UL).
   3. SUBMITTALS
      1. Submit under provisions of Section 013000.
      2. Product Data: Manufacturer's data sheets on each product to be used, including:
         1. Preparation instructions and recommendations.
         2. Storage and handling requirements and recommendations.
         3. Installation methods.
   4. QUALITY ASSURANCE
      1. Manufacturer Qualifications:
         1. Minimum 20 years of experience in design, engineering, manufacture and support of specified system and components.
      2. Product Requirements:
         1. Pipe Trace - Temperature Maintenance: Consult the Manufacturers Pipe Tracing Design Guide to determine recommended w/ft. for installation. Design shall consider a maintenance temperature of 110˚F, lowest ambient temperature, pipe size, insulation type and thickness, and environmental conditions.
         2. Heating equipment furnished under this section shall be supplied by a single manufacturer.
         3. UL Listed or CSA Certified Mineral Insulated (MI) pipe or tank tracing cable assemblies:
            1. MI pipe or tank tracing cable assembly shall be factory assembled, immersed in water for a minimum of 12 hours, and then tested for insulation resistance, high potential breakdown and continuity before leaving the factory.
         4. FM Approved Constant Wattage cable.
         5. UL Listed Thermostat and Contactor panel.
         6. UL Listed, CSA Certified or FM Approved Control/Monitor Panel.
   5. DELIVERY, STORAGE, AND HANDLING
      1. Store products in manufacturer's unopened packaging until ready for installation.
      2. Store and dispose of solvent-based materials, and materials used with solvent-based materials, in accordance with requirements of local authorities having jurisdiction.
   6. PROJECT CONDITIONS
      1. Coordinate installation of heating cable with Electrical Contractor and Mechanical Contractor.
      2. Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer. Do not install products under environmental conditions outside manufacturer's limits.
2. PRODUCTS
   1. MANUFACTURERS
      1. System shall be manufactured by:

Delta-Therm Corporation, 6711 Sands Rd Suite A, Crystal Lake, IL 60014, Phone: 800-526-7887, Fax: 847-526-4456, Email: info@Delta-Therm.com, Web: www.Delta-Therm.com

* + 1. Requests for substitutions will be considered in accordance with provisions of Section 016000.
  1. HEATING CABLE
     1. Factory Terminated Mineral Insulated (MI) Cable assembly:
        1. UL Listed Mineral-Insulated, copper or stainless steel sheathed, series resistance heating cable.
        2. Single conductor or dual conductor configuration.
        3. Insulator shall be Magnesium Oxide.
        4. Fiberglass insulator is not permitted.
        5. No combustible materials between conductor wire and ground sheath.
        6. Cross section of heated portion of cable not to exceed 0.4 inch (10 mm).
        7. Cable heater construction shall consist of factory termination to stranded connection leads.
        8. Connection leads shall be of enough length to reach junction boxes or power panel as shown on detailed drawings. Connection leads shall be of stranded wire to provide maximum flexibility for ease in pulling to junction boxes or panel. Only connection leads in conduit shall exit from heated zone.
        9. Cable rating shall be:
           1. 120 VAC
           2. 208 VAC
           3. 240 VAC
           4. 277 VAC
           5. 480 VAC
     2. Field Terminated Constant Watt (CW) Cable assembly:
        1. The constant watt cable construction shall be parallel resistance 12 AWG stranded nickel-plated copper bus wires individually encased in:
           1. Extruded FEP Teflon™ jacket (type PF High Temp cable).
           2. Sintered PTFE Teflon™ jacket (type PT Ultra High Temp cable).
        2. A nichrome wire heating element shall be wrapped around the jacket and fastened to alternating bus wires at 24” or 48” (zone lengths vary between models).
        3. The jacket and nichrome wire construction shall be encased in a color-coded insulated jacket and identified with a marker.
        4. Cable shall be terminated using approved Manufacturers power connection and end termination kits.
        5. The Stainless-Steel ground braid shall be used as a ground path per NEC requirements as stated in article 427-23.
        6. Cable shall have a maximum maintenance temperature of at least 200° F and a maximum exposure temperature of at least 400° F.
           1. 120 VAC
           2. 208 VAC
           3. 240 VAC
           4. 277 VAC
           5. 480 VAC
  2. CONTROLS
     1. Single Circuit type Monitoring Control:
        1. Control input voltages shall be 120VAC, 208VAC, 240VAC, or 277VAC.
        2. Enclosure shall be NEMA 4X.
        3. Control shall have adjustable setpoint temperature.
        4. Control shall monitor pipe temperature or ambient temperature.
        5. Control shall have 30mA ground fault alarm as required.
        6. Control shall have temperature sensor failure alarm.
        7. Control shall have low and high temperature alarm.
        8. Control shall monitor current and have a low current alarm.
     2. Thermostat

1. Thermostat shall be Ambient or line sensing.

2. Enclosure shall be rated for the environment

3. Thermostat shall be set to activate at the maintenance temperature

4. Thermostat rating shall be:

* + - * 1. 120 VAC
        2. 208 VAC
        3. 240 VAC
        4. 277 VAC
    1. Power Control Panel with G.F.E.P:
       1. Controller shall have:
          1. NEMA 4X rated panel enclosure with one Ground Fault protective device for all circuit.
          2. One white “Power On” LED, one red “Control On” LED, and one yellow “Ground Fault Indicator” LED on panel door.
          3. Power Control Panel Model shall be:

GFEP-2-N

GFEP-4-N

GFEP-6-N

GFEP-8-N

GFEP-12-N

* + 1. Custom Control Panel Specifications
  1. ACCESSORIES
     + 1. Power connection kits, splice kits, end termination kits, fiberglass tape, caution labels, aluminum tape, stainless- steel banding, monitor light.

PART 3 EXECUTION

3.1 EXAMINATION

* + 1. Installer to verify field measurements are as shown on Drawings.
    2. Installer to verify that required power is available, in proper location, and ready for use.
    3. Do not begin installation until piping has been properly prepared.

3.2 PREPARATION

* + 1. Clean surfaces prior to installation.
    2. Prepare surfaces using the methods recommended by the manufacturer.

3.3 INSTALLATION

* + 1. Complete installation shall conform to all applicable codes.
    2. Install heating cables in accordance with detailed layout drawings and manufacturer's instructions.
    3. Band heating cable to pipe with tape wraps approximately every 12 inches.
    4. Locate heating cable on pipe per manufacturer's instructions.
    5. Mineral Insulated (MI) Cable Installation  
        Install per Manufacturer’s Instructions.
       1. Pull stranded M.I. connection leads through conduit from the M.I. Assembly supplied conduit body to junction boxes.
       2. Do not pinch or make sharp bends in cable.
       3. Tape heating cable hot-cold junction to pipe.
    6. Constant Watt (CW) Cable Installation  
        Install per Manufacturer’s Instructions.
       1. Identify the heating zone (every 24” to 48”) before cutting cable leaving at least 12 inches for terminating the cable.
       2. Terminate non-power end of cable per termination kit instructions.
       3. Do not pinch or make sharp bends in cable.
       4. At power termination mount power connection standoff and junction box per power termination kit instructions. The electrical connection shall be made per the termination kit instruction and all local codes.
       5. Install monitor lights per the kit instruction and all applicable codes.
    7. Thermostatic Control System
       1. Thermostatic sensor to be attached to the pipe wall, 90˚ to the heat trace cable, under insulation.
       2. 30mA ground fault protection to be provided by the contactor/relay panel, or controller.
       3. Thermostat/Control to be set to maintain a constant pipe wall temperature of 110˚F.
  1. FIELD QUALITY CONTROL
     1. Test continuity of heating cable. Perform Insulation Resistance (IR) or “Megger” test on each heating cables before, during, and after pipe insulation has been installed. Insulation resistance should be greater than 10 megohms.
     2. Measure voltage and current at each unit after pipe installation is installed.
     3. Enter the total resistance and insulation resistance readings on the warranty card.
     4. Annually check system for loose or damaged cable.

3.5 ADJUSTING AND CLEANING

* + 1. Adjust system controls and instruct Owner/Operator.

3.6 PROTECTION

* + 1. Protect installed products until completion of project.
    2. Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION